## Funksjonstabell_Systemkart
ScopeGroup | fault_loc_key | Component ID | Component Name | Type | Data Type | Measured / Status Signals | Upstream Node | Downstream Node | BranchTo | ParentComponent | MeasuresAt | LinkedTo | OperationalState | SensorIntegrity_Utility | StatusConsistency_Utility | CyberSecurity_Utility | DataIntegrity_Utility | DigitalTwinImpact_Utility | Comment
A- | A | A-B1 | Circuit breaker | Breaker | Binary | Status (open/closed) |  | L1 |  |  |  |  | Open:no current; Closed:load current present | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 | Main switch device
A- | A | A-B2 | Earthing switch | Switch | Binary | Status (open/closed) |  |  | A-B1 |  |  |  | May only be closed when upstream breaker open and line de-energized | 1.0 | 1.0 | 1.0 | 1.0 | 0.7 | Ensures personnel safety; interlocked with A-B2. Also used for maintenance grounding
A- | A | A-M1 | Current meter | Sensor | Continuous | A, I_L1 |  |  |  | A-B1 | L1 |  |  | 0.9 | 0.7 | 0.7 | 0.9 | 0.8 | Energy monitoring
A- | A | A-M2 | Voltage meter | Sensor | Continuous | kV, U_L1–L2 |  |  |  | A-B1 | L1 |  | Normal voltage ≈ 22 kV ± 5 %; I > 0 when CB = closed | 0.9 | 0.7 | 0.7 | 0.9 | 0.8 | Energy monitoring
A- | A | A-M3 | Power meter | Sensor | Continuous | MW, P |  |  |  | A-B1 | L1 |  |  | 0.9 | 0.7 | 0.7 | 0.9 | 0.8 | Energy monitoring
A- | A | A-S1 | Earth-fault Indicator | Indicator | Binary | Normal / Start |  |  |  | A-B1 | L1 |  | Triggered:fault current detected | 0.5 | 0.5 | 0.3 | 0.7 | 0.3 | Fault localization
A- | A | A-S2 | Earth-fault Indicator | Indicator | Binary | Normal / Frakopling |  |  |  | A-B1 | L1 |  | Triggered:fault current detected | 0.5 | 0.5 | 0.3 | 0.7 | 0.3 | Fault localization
A- | A | A-S3 | Short-circuit indicator | Indicator | Binary | Normal / Start |  |  |  | A-B1 | L1 |  | Triggered:fault current detected. I> | 0.5 | 0.5 | 0.3 | 0.7 | 0.3 | Fault localization
A- | A | A-S4 | Short-circuit indicator | Indicator | Binary | Normal / Frakopling |  |  |  | A-B1 | L1 |  | Triggered:fault current detected. I> | 0.5 | 0.5 | 0.3 | 0.7 | 0.3 | Fault localization
A- | A | A-S5 | Short-circuit indicator | Indicator | Binary | Normal / Frakopling |  |  |  | A-B1 | L1 |  | Triggered:fault current detected. I>> | 0.5 | 0.5 | 0.3 | 0.7 | 0.3 | Fault localization
A- | A | A-COM | IEC104 | Communication | Binary | OK / FEIL |  |  |  | A-B1 | A | A-B1,A-M1,A-M2,A-M3,A-S1,A-S2,A-S3,A-S4,A-S5 | FAIL:data unreliable | 0.7 | 1.0 | 1.0 | 1.0 | 0.5 | Fiber. Impacts monitoring reliability
L1 |  | L1 | Line Section | LineSection |  |  | A-B1 | B-B2
B- | B | B-B1 | Earthing switch | Switch | Binary | Status (open/closed) |  |  | B-B2 |  |  |  | May only be closed when upstream breaker open and line de-energized | 1.0 | 1.0 | 1.0 | 1.0 | 0.7 | Ensures personnel safety; interlocked with A-B2. Also used for maintenance grounding
B- | B | B-B2 | Load break switch | Switch | Binary | Status (open/closed) | L1 | B-B4 | B-B3 |  |  |  | Open:no current; Closed:load current present | 0.3 | 0.5 | 0.5 | 0.5 | 0.3 | Main switch device
B- | B | B-B3 | Load break switch (sectionalizing point) | Switch | Binary | Status (open/closed) |  |  | L21 |  |  |  | Normally open(used for backup or reconfiguration) | 0.3 | 0.5 | 0.5 | 0.5 | 0.5 | Boundary point; downstream not modeled
B- | B | B-B4 | Load break switch | Switch | Binary | Status (open/closed) | B-B2 | L2 |  |  |  |  | Open:no current; Closed:load current present | 0.3 | 0.5 | 0.5 | 0.5 | 0.3 | Main switch device
B- | B | B-B5 | Earthing switch | Switch | Binary | Status (open/closed) |  |  | B-B4 |  |  |  | May only be closed when upstream breaker open and line de-energized | 1.0 | 1.0 | 1.0 | 1.0 | 0.7 | Ensures personnel safety; interlocked with A-B2. Also used for maintenance grounding
B- | B | B-S1 | Earth-fault Indicator | Indicator | Binary | Normal / Frakopling |  |  |  | B-B4 | L2 |  | Triggered:fault current detected | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | Fault localization
B- | B | B-COM | IEC104 | Communication | Binary | OK / FEIL |  |  |  | B-B2 | B | B-B1,B-B2,B-B3,B-B4,B-B5,B-S1 | FAIL:data unreliable | 0.3 | 0.5 | 0.5 | 0.3 | 0.3 | 4G-modem. Impacts monitoring reliability
L21 | B | L21 | Line Section | LineSection | [5 empty] | B-B3
L2 |  | L2 | Line Section | LineSection |  |  | B-B4 | C-B2
C- | C | C-B1 | Earthing switch | Switch | Binary | Status (open/closed) |  |  | C-B2 |  |  |  | May only be closed when upstream breaker open and line de-energized | 1.0 | 1.0 | 1.0 | 1.0 | 0.7 | Ensures personnel safety; interlocked with A-B2. Also used for maintenance grounding
C- | C | C-B2 | Load break switch | Switch | Binary | Status (open/closed) | L2 | C-B3 |  |  |  |  | Open:no current; Closed:load current present | 0.3 | 0.5 | 0.5 | 0.3 | 0.3 | Main switch device
C- | C | C-B3 | Circuit breaker | Breaker | Binary | Status (open/closed) | C-B2 | C-B4 |  |  |  |  | Open:no current; Closed:load current present | 0.3 | 0.5 | 0.5 | 0.3 | 0.3 | Main protection device
C- | C | C-B4 | Load break switch | Switch | Binary | Status (open/closed) | C-B3 | L3 |  |  |  |  | Open:no current; Closed:load current present | 0.3 | 0.5 | 0.5 | 0.3 | 0.3 | Main switch device
C- | C | C-B5 | Earthing switch | Switch | Binary | Status (open/closed) |  |  | C-B4 |  |  |  | May only be closed when upstream breaker open and line de-energized | 1.0 | 1.0 | 1.0 | 1.0 | 0.7 | Ensures personnel safety; interlocked with A-B2. Also used for maintenance grounding
C- | C | C-M1 | Current meter | Sensor | Continuous | A, I_R–0 |  |  |  | C-B4 | L3 |  |  | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | Energy monitoring
C- | C | C-M2 | Power meter | Sensor | Continuous | MW |  |  |  | C-B4 | L3 |  | P = U × I × cosφ | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | Energy monitoring
C- | C | C-M3 | Voltage meter | Sensor | Continuous | kV, U0 |  |  |  | C-B4 | L3 |  |  | 0.3 | 0.3 | 0.3 | 0.3 | 0.5
C- | C | C-M4 | Voltage meter | Sensor | Continuous | kV, U_L1–L2 |  |  |  | C-B4 | L3 |  | Normal voltage ≈ 22 kV ± 5 %; I > 0 when CB = closed | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | Energy monitoring
C- | C | C-S1 | Earth-fault Indicator | Indicator | Binary | Normal / Varsel |  |  |  | C-B4 | L3 |  | Triggered:fault current detected | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | Fault localization
C- | C | C-S2 | Short-circuit indicator | Indicator | Binary | 0 = normal, 1 = fault |  |  |  | C-B4 | L3 |  | Triggered:fault current detected. I> | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | Fault localization
C- | C | C-COM | IEC104 | Communication | Binary | OK / FEIL |  |  |  | C-B2 | C | C-B1,C-B2,C-B3,C-B4,C-B5,C-S1,C-S2,C-M1,C-M2,C-M3,C-M4 | FAIL:data unreliable | 0.3 | 0.5 | 0.5 | 0.3 | 0.3 | Digital Radio. Impacts monitoring reliability
L3 | IDK2 | L3 | Line Section | LineSection |  |  | C-B4 | D-B1
L3 | IDK2 | IDK2-S1 | Earth-fault Indicator | Indicator | Binary | 0 = normal, 1 = RED transient fault |  |  |  | L3 | L3 |  | Triggered:fault current detected | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | Fault localization
L3 | IDK2 | IDK2-S2 | Earth-fault Indicator | Indicator | Binary | 0 = normal, 1 = RED fault |  |  |  | L3 | L3 |  | Triggered:fault current detected | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | Fault localization
L3 | IDK2 | IDK2-S3 | Earth-fault Indicator | Indicator | Binary | 0 = normal, 1 = GREEN transient fault |  |  |  | L3 | L3 |  | Triggered:fault current detected | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | Fault localization
L3 | IDK2 | IDK2-S4 | Earth-fault Indicator | Indicator | Binary | 0 = normal, 1 = GREEN fault |  |  |  | L3 | L3 |  | Triggered:fault current detected | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | Fault localization
L3 | IDK2 | IDK2-S5 | Short-circuit indicator | Indicator | Binary | 0 = normal, 1 = transient fault |  |  |  | L3 | L3 |  | Triggered:fault current detected | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | Fault localization
L3 | IDK2 | IDK2-S6 | Short-circuit indicator | Indicator | Binary | 0 = normal, 1 = fault |  |  |  | L3 | L3 |  | Triggered:fault current detected | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | Fault localization
L3 | IDK2 | IDK2-COM | SMS | Communication | Binary | OK / FEIL |  |  |  | L3 | IDK2 | IDK2-S1,IDK2-S2,IDK2-S3,IDK2-S4,IDK2-S5,IDK2-S6 | FAIL:data unreliable | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | Edge. Impacts monitoring reliability
D- | D | D-B1 | Load break switch | Switch | Binary | Status (open/closed) | L3 | L4 |  |  |  |  | Open:no current; Closed:load current present | 0.3 | 0.3 | 0.5 | 0.3 | 0.3 | Main switch device
D- | D | D-M1 | Voltage meter | Sensor | Discrete | kV, U_L1–L2 |  |  |  | D-B1 | L4 |  | Normal voltage ≈ 22 kV ± 5 %; I > 0 when CB = closed | 0.3 | 0.3 | 0.5 | 0.3 | 0.3 | Feeder-level measurement
D- | D | D-COM | Procol | Communication | Binary | OK / FEIL |  |  |  | D-B1 | D | D-B1,D-M1 | FAIL:data unreliable | 0.3 | 0.3 | 0.5 | 0.3 | 0.5 | Analog Radio. Impacts monitoring reliability
L4 |  | L4 | Line Section | LineSection |  |  | D-B1 | E-B1
E- | E | E-B1 | Load break switch | Switch | Binary | Status (open/closed) | L4 | L5 |  |  |  |  | Open:no current; Closed:load current present | 0.3 | 0.3 | 0.5 | 0.3 | 0.3 | Main switch device
E- | E | E-S1 | Earth-fault Indicator | Indicator | Binary | 0 = normal, 1 = RED transient fault |  |  |  | E-B1 | L5 |  | Triggered:fault current detected | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | Fault localization
E- | E | E-S2 | Earth-fault Indicator | Indicator | Binary | 0 = normal, 1 = RED fault |  |  |  | E-B1 | L5 |  | Triggered:fault current detected | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | Fault localization
E- | E | E-S3 | Earth-fault Indicator | Indicator | Binary | 0 = normal, 1 = GREEN transient fault |  |  |  | E-B1 | L5 |  | Triggered:fault current detected | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | Fault localization
E- | E | E-S4 | Earth-fault Indicator | Indicator | Binary | 0 = normal, 1 = GREEN fault |  |  |  | E-B1 | L5 |  | Triggered:fault current detected | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | Fault localization
E- | E | E-S5 | Short-circuit indicator | Indicator | Binary | 0 = normal, 1 = transient fault |  |  |  | E-B1 | L5 |  | Triggered:fault current detected | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | Fault localization
E- | E | E-S6 | Short-circuit indicator | Indicator | Binary | 0 = normal, 1 = fault |  |  |  | E-B1 | L5 |  | Triggered:fault current detected | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | Fault localization
E- | E | E-COM | IEC104 | Communication | Binary | OK / FEIL |  |  |  | E-B1 | E | E-B1,E-S1,E-S2,E-S3,E-S4,E-S5,E-S6 | FAIL:data unreliable | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 4G-modem. Impacts monitoring reliability
L5 |  | L5 | Line Section | LineSection |  |  | E-B1 | F-B2
F- | F | F-B1 | Load break switch (sectionalizing point) | Switch | Binary | Status (open/closed) |  |  | L61 |  |  |  | Open:no current; Closed:load current present | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | Main switch device
F- | F | F-B2 | Load break switch | Switch | Binary | Status (open/closed) | L5 | F-B3 | F-B1 |  |  |  | Normally closed. Open -> no current for Line section L61 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | Boundary point; downstream not modeled. Downstream: Line section L61 (Short spur, 2km)
F- | F | F-B3 | Load break switch | Switch | Binary | Status (open/closed) | F-B2 | L6 |  |  |  |  | Open:no current; Closed:load current present | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | Main switch device
F- | F | F-COM | IEC104 | Communication | Binary | OK / FEIL |  |  |  | F-B2 | F | F-B1,F-B2,F-B3 | FAIL:data unreliable | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 4G-modem. Impacts monitoring reliability
L6 | IDK5 | L6 | Line Section | LineSection |  |  | F-B3 | G-B1
L61 | IDK8 | L61 | Line Section | LineSection | [5 empty] | F-B1
L61 | IDK8 | IDK8-S1 | Earth-fault Indicator | Indicator | Binary | 0 = normal, 1 = RED transient fault |  |  |  | L61 | L61 |  | Triggered:fault current detected | 0.5 | 0.3 | 0.3 | 0.3 | 0.5 | Fault localization
L61 | IDK8 | IDK8-S2 | Earth-fault Indicator | Indicator | Binary | 0 = normal, 1 = RED fault |  |  |  | L61 | L61 |  | Triggered:fault current detected | 0.5 | 0.3 | 0.3 | 0.3 | 0.5 | Fault localization
L61 | IDK8 | IDK8-S3 | Earth-fault Indicator | Indicator | Binary | 0 = normal, 1 = GREEN transient fault |  |  |  | L61 | L61 |  | Triggered:fault current detected | 0.5 | 0.3 | 0.3 | 0.3 | 0.5 | Fault localization
L61 | IDK8 | IDK8-S4 | Earth-fault Indicator | Indicator | Binary | 0 = normal, 1 = GREEN fault |  |  |  | L61 | L61 |  | Triggered:fault current detected | 0.5 | 0.3 | 0.3 | 0.3 | 0.5 | Fault localization
L61 | IDK8 | IDK8-S5 | Short-circuit indicator | Indicator | Binary | 0 = normal, 1 = transient fault |  |  |  | L61 | L61 |  | Triggered:fault current detected | 0.5 | 0.3 | 0.3 | 0.3 | 0.5 | Fault localization
L61 | IDK8 | IDK8-S6 | Short-circuit indicator | Indicator | Binary | 0 = normal, 1 = fault |  |  |  | L61 | L61 |  | Triggered:fault current detected | 0.5 | 0.3 | 0.3 | 0.3 | 0.5 | Fault localization
L61 | IDK8 | IDK8-COM | SMS | Communication | Binary | OK / FEIL |  |  |  | L61 | IDK8 | IDK8-S1,IDK8-S2,IDK8-S3,IDK8-S4,IDK8-S5,IDK8-S6 | FAIL:data unreliable | 0.5 | 0.3 | 0.3 | 0.3 | 0.5 | Edge. 4G-modem. Impacts monitoring reliability
L6 | IDK5 | IDK5-S1 | Earth-fault Indicator | Indicator | Binary | 0 = normal, 1 = RED transient fault |  |  |  | L6 | L6 |  | Triggered:fault current detected | 0.5 | 0.3 | 0.3 | 0.3 | 0.5 | Fault localization
L6 | IDK5 | IDK5-S2 | Earth-fault Indicator | Indicator | Binary | 0 = normal, 1 = RED fault |  |  |  | L6 | L6 |  | Triggered:fault current detected | 0.5 | 0.3 | 0.3 | 0.3 | 0.5 | Fault localization
L6 | IDK5 | IDK5-S3 | Earth-fault Indicator | Indicator | Binary | 0 = normal, 1 = GREEN transient fault |  |  |  | L6 | L6 |  | Triggered:fault current detected | 0.5 | 0.3 | 0.3 | 0.3 | 0.5 | Fault localization
L6 | IDK5 | IDK5-S4 | Earth-fault Indicator | Indicator | Binary | 0 = normal, 1 = GREEN fault |  |  |  | L6 | L6 |  | Triggered:fault current detected | 0.5 | 0.3 | 0.3 | 0.3 | 0.5 | Fault localization
L6 | IDK5 | IDK5-S5 | Short-circuit indicator | Indicator | Binary | 0 = normal, 1 = transient fault |  |  |  | L6 | L6 |  | Triggered:fault current detected | 0.5 | 0.3 | 0.3 | 0.3 | 0.5 | Fault localization
L6 | IDK5 | IDK5-S6 | Short-circuit indicator | Indicator | Binary | 0 = normal, 1 = fault |  |  |  | L6 | L6 |  | Triggered:fault current detected | 0.5 | 0.3 | 0.3 | 0.3 | 0.5 | Fault localization
L6 | IDK5 | IDK5-COM | SMS | Communication | Binary | OK / FEIL |  |  |  | L6 | IDK5 | IDK5-S1,IDK5-S2,IDK5-S3,IDK5-S4,IDK5-S5,IDK5-S6 | FAIL:data unreliable | 0.5 | 0.5 | 0.3 | 0.3 | 0.5 | Edge. Impacts monitoring reliability
G- | G | G-B1 | Load break switch | Switch | Binary | Status (open/closed) | L6 | L7 |  |  |  |  | Open:no current; Closed:load current present | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | Main switch device
G- | G | G-S1 | Earth-fault Indicator | Indicator | Binary | 0 = normal, 1 = RED transient fault |  |  |  | G-B1 | L7 |  | Triggered:fault current detected | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | Fault localization
G- | G | G-S2 | Earth-fault Indicator | Indicator | Binary | 0 = normal, 1 = RED fault |  |  |  | G-B1 | L7 |  | Triggered:fault current detected | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | Fault localization
G- | G | G-S3 | Earth-fault Indicator | Indicator | Binary | 0 = normal, 1 = GREEN transient fault |  |  |  | G-B1 | L7 |  | Triggered:fault current detected | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | Fault localization
G- | G | G-S4 | Earth-fault Indicator | Indicator | Binary | 0 = normal, 1 = GREEN fault |  |  |  | G-B1 | L7 |  | Triggered:fault current detected | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | Fault localization
G- | G | G-S5 | Short-circuit indicator | Indicator | Binary | 0 = normal, 1 = transient fault |  |  |  | G-B1 | L7 |  | Triggered:fault current detected | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | Fault localization
G- | G | G-S6 | Short-circuit indicator | Indicator | Binary | 0 = normal, 1 = fault |  |  |  | G-B1 | L7 |  | Triggered:fault current detected | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | Fault localization
G- | G | G-COM | IEC104 | Communication | Binary | OK / FEIL |  |  |  | G-B1 | G | G-B1,G-S1,G-S2,G-S3,G-S4,G-S5,G-S6 | FAIL:data unreliable | 0.5 | 0.5 | 0.3 | 0.3 | 0.2 | Digital Radio.Impacts monitoring reliability
L7 |  | L7 | Line Section | LineSection |  |  | G-B1 | H-B1
H- | H | H-B1 | Load break switch | Switch | Binary | Status (open/closed) | L7 | L8 |  |  |  |  | Normally open | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | L8, out of model scope
H- | H | H-COM | IEC104 | Communication | Binary | OK / FEIL |  |  |  | H-B1 | H | H-B1 | FAIL:data unreliable | 0.3 | 0.5 | 0.3 | 0.3 | 0.1 | 4G-modem. Impacts monitoring reliability
L8 |  | L8 | Line Section | LineSection |  |  | H-B1

## Ark2
Hva «samband FEIL / OK» egentlig representerer
Dette er en aggregert indikator for kommunikasjonens tilstand, og dekker som regel:
CRC-feil (mismatch i pakkeintegritet),
tapte datapakker,
manglende respons fra RTU eller sensor,
feil på linje eller radiolink.
Så funksjonelt sett kan du tenke på den som en «kommunikasjonshelse»-variabel:
OK = 1 → Kommunikasjon fungerer, data er til å stole på
FEIL = 0 → Kommunikasjonsfeil eller mistanke om manipulering
Kort oppsummert
«Samband: FEIL/OK» er en binær indikator som summerer resultatet av underliggende integritetskontroller (som CRC). Den kan brukes som en viktig statusvariabel i KI-modellen for å fange kommunikasjonsfeil, avbrudd eller manipulasjon i måledata.»
Riktig og tydelig begrepsbruk for deg (kraftnett + ML)
Betegnelse | Hva det betyr | Eksempler (SCADA / 22 kV-nett) | Typisk datatype i ML
Binary (binær) | To mulige verdier (0/1, TRUE/FALSE, INNE/UTE) | Bryterstatus, samband OK/FEIL, alarm aktiv | Kodes som 0/1 (boolsk feature)
Discrete (diskret) | Avgrenset, men flere trinn – ikke kontinuerlig | Lasttrinn 1–5, tap position 0–10, temperaturklasse 1–4 | Heltall / kategoriske numeriske features
Continuous (kontinuerlig) | Måleverdier med reell skala | Spenning (22.4 kV), strøm (130 A), effekt (2.4 MW) | Flyttall / numerisk feature
Categorical (kategorisk) | Navn, ikke tall – grupper eller moduser | Driftmodus: Auto / Manuell, Trafo-type | Må kodes (one-hot / label encoding)
Relational (relasjonell) | Angir sammenhenger mellom komponenter (topologi) | Linje L1 kobler bryter B1–B2, Sensor S1 på node N2 | Brukes i GNN eller som topologisk struktur
Eksempler i din kontekst
Signal | Datatype | Forklaring
Bryterstatus | Binary | 0 = åpen, 1 = lukket
Samband | Binary | OK / FEIL
Tap-posisjon (på trafo) | Discrete | 0–10 trinn
Laststrøm | Continuous | Målt i ampere, kontinuerlig verdi
Driftmodus | Categorical | Auto / Manuell
L1 ↔ B1 ↔ B2 | Relational | Nettverkstilknytning
Realitet: Forskjellige typer anlegg/ulik utstyrt, forskjellig typer kommunikasjon
Seksjonering/delingspunkt
Datakvalitet: data og ikke minst klokkeslett. Målingene L1-L2, Strøm Il1
Jordfeilindikator/KS-ind. for NS, riktig innstilt?

## Ark3
Nøkkel | Betydning
Upstream | Komponent som ligger elektrisk foran (mot kilde/trafo). | 🔹 5. Anbefalt fremgangsmåte videre Definer disse fire kolonnene i funksjonstabellen nå: Utility_Cyber Utility_Sensor Utility_Status Utility_Operational Bruk dem både i AI-evalueringen og i Digital Twin-delen. Dette gjør at du kan dokumentere hvordan AI-modellen forbedrer twinens trustworthiness og data integrity. Når du evaluerer modellene senere, kan du si: “The LSTM model achieved higher Utility_Cyber and Utility_Sensor values, indicating improved reliability of the digital twin compared to the baseline Transformer model.”
Downstream | Komponent(er) som forsynes videre fra denne.
DownstreamSection | Navn på ny linjeseksjon hvis den går videre (f.eks. L2).
BranchTo | Samme som over, men eksplisitt hvis forgreningen leder til ny radial.
InterlockedWith | Mekanisk/elektrisk interlock; viktig for sikker drift.
BoundaryOf | Seksjon som bryteren definerer grensen for.
MeasuresAt | Punkt der sensor/måler er tilknyttet.
LinkedTo | Generell kobling (for kommunikasjon, RTU osv.).
Scope | Internal eller External – markerer om relasjonen ligger innenfor prosjektets modell

## Utility
Utility-type | Formål | Relevans i oppgaven
Utility_Cyber | Hvor viktig det er å oppdage cyberangrep (False Data Injection, spoofing) | Evaluerer hvor godt modellen beskytter SCADA-integritet
Utility_Sensor | Hvor mye sensorfeil påvirker resultatet | Evaluerer robusthet mot fysiske feil / målefeil
Utility_Status | Hvor viktig korrekt bryterposisjon og statusindikatorer er | Evaluerer hvor godt modellen forstår operasjonell kontekst
Utility_Operational | Kritikalitet for driftsstabilitet (nettseksjon, bryter, node) | Brukes til å vekte påvirkning på stabilitet og risiko
(valgfritt) Utility_Safety | Personsikkerhet og jordingslogikk | Relevans for feltoperasjoner, ikke bare data
Felles referanse for alle modeller Alle modellene dine (f.eks. LSTM, Autoencoder, Transformer, Hybrid) vil produsere resultater som: “anomaly detected / not detected”, “confidence”, eller “reconstruction error”. Men for å vurdere hva som faktisk er bra, må du måle effekten i form av utility — altså hvor nyttig det er å oppdage den aktuelle hendelsen. Det kan du bare gjøre hvis alle modellene vurderes mot de samme dimensjonene.
Modell | Precision | Recall | Utility_Cyber | Utility_Sensor | Utility_Status
LSTM | 0.87 | 0.81 | 0.92 | 0.70 | 0.78
Transformer | 0.89 | 0.79 | 0.94 | 0.73 | 0.76
Hybrid | 0.88 | 0.84 | 0.91 | 0.75 | 0.81
Component ID | Type | Utility_Cyber | Utility_Sensor | Utility_Status | Utility_Safety | Utility_Operational
A-B1 | Breaker | 5 | 2 | 5 | 4 | 5
A-B2 | Earthing Switch | 2 | 1 | 4 | 5 | 3
A-M1 | Current Meter | 3 | 5 | 1 | 2 | 3
A-S1 | Fault Indicator | 3 | 4 | 3 | 3 | 3

## Ark5
Mål | Hva du ønsker å oppnå | Hvorfor viktig
1️⃣ Oppdage sensor-, indikator- og status-avvik | Fange feil i målinger og posisjonsindikatorer som kan skape feil tilstandsforståelse | Forbedrer situasjonsforståelse og reduserer falske beslutninger i SCADA og Digital Twin
2️⃣ Oppdage og reagere på cyberangrep (FDI, spoofing, DoS) | Beskytte dataintegritet og sikre at AI-modellen gjenkjenner manipulerte signaler | Opprettholder Digital Twin-ens pålitelighet og operasjonell sikkerhet
3️⃣ Identifisere avvik som påvirker nettmodellen / Digital Twin | Oppdage feil som fører til uoverensstemmelse mellom fysisk nett og twin | Sørger for at twinens simuleringer og beslutningsstøtte faktisk reflekterer virkeligheten
Utility-kolonne | Formål | Knyttet til hovedmål
SensorIntegrity_Utility | Hvor kritisk korrekt måledata (I, U, P, etc.) er for systemets beslutninger | 1
StatusConsistency_Utility | Hvor viktig riktige bryter- og indikatorstatus er for å tolke driftstilstanden | 1
CyberSecurity_Utility | Hvor alvorlig påvirkning cyberangrep eller datamanipulasjon har | 2
DataIntegrity_Utility | Hvor følsomt systemet er for tap, støy eller korrupt SCADA-data | 2 + 3
DigitalTwinImpact_Utility | Hvor mye en feil i denne komponenten påvirker twinens modell og simuleringer | 3
Anomali-type | Påvirker | Relevante utilities
Sensorfeil (måledata ute av drift, støy) | Modellens observasjon og twinens datastrøm | SensorIntegrity_Utility, DataIntegrity_Utility
Indikator-/statusfeil (f.eks. bryter står feil i SCADA) | Nettmodell og topologisk tilstand | StatusConsistency_Utility, DigitalTwinImpact_Utility
Cyberangrep (False Data Injection, spoofing, DoS) | SCADA- og twin-integritet, beslutningsgrunnlag | CyberSecurity_Utility, DataIntegrity_Utility, DigitalTwinImpact_Utility
Nettmodell-avvik (mismatch mellom fysisk nett og twin) | Beslutningsstøtte og prediktiv analyse | DigitalTwinImpact_Utility (kombinert effekt av de andre)